## parameter list
1.Transmission Format
Baud Rate |  |  | 4800bps
Start bit |  |  | 1
Byte width |  |  | 8
Parity |  |  | N
Stop bits |  |  | 1
Slave address |  |  | 97
2.Packet Format
Address | Function |  |  | Data | CRC checksum
8bits | 8bits 03: Function of reading multi registers 16: Function of presenting multi registers |  |  | N*8bits | 16bits
3.Data types
Data Types | Description
TEMP2 | unsigned byte; length: 8 bits; unit: 1; when displaying 1, the data transmitted 1.
TEMP3 | unsigned byte; accuracy: 0.5℃; formula: T*2 + 60; temperature range: -30~97℃(when displaying 25℃, according to the above formula, the data transitted by protocol is110)
TEMP4 | unsigned byte; accuracy: 0.1bar; formula: T*10; range: 0~50bar (when displaying 25bar, according to the above formula, the data transitted by protocol is 250)
TEMP5 | unsigned byte; accuracy: 1℃; formula: T + 30; temperature range: -30~224℃
4.Mailing address
| Type | Factory parameters——modbus address list |  |  |  |  | S.No. | state parameter
| C Parameters | function | default | range | type | Address | U01 | water inlet temperature
| C01 | Outlet anti-freezing temperature point | 5℃ | 1~10 | TEMP3 | 1001 | U02 | water outlet temperature
| C02 | Low pressure value of anti-freezing | 0bar | 0~10 | TEMP4 | 1002 | U03 | suction temperature
| C03 | Return difference of anti-freezing protection | 2℃ | 0~10 | TEMP3 | 1003 | U04 | exhaust temperature
| C04 | Minimum working temperature of heat pump | -20℃ | -30~10 | TEMP3 | 1004 | U05 | ambient temperature
| C05 | Exhaust over-temperature protection value | 110℃ | 80~130 | TEMP5 | 1005 | U06 | Coil temperature
| C06 | Spray valve starting temperature | 35℃ | 10~50 | TEMP3 | 1006 | U07 | Low pressure
| C07 | Compressor frequency control/ Value P | 5 | 1~100 | TEMP2 | 1007 | U08 | High pressure
| C08 | Compressor frequency/ Value I | 1 | 1~100 | TEMP2 | 1008 | U09 | electronic expansion valve
| C09 | Compressor frequency control/ Value D | 5 | 0~100 | TEMP2 | 1009 | U10 | actual frequency
| C10 | Compressor min. frequency | 30 | 20~60 | TEMP2 | 1010 | U11 | set frequency
| C11 | Compressor max. frequency | 90 | 30~120 | TEMP2 | 1011 | U12 | suction overheat
| C12 | Heating quitting/coil set point of quitting heating | 13℃ | 1~40 | TEMP3 | 1012 | U13 | exhaust overheat
| C13 | Heating quitting/defrosting set point | 25bar | 1~25 | TEMP4 | 1013 | U14 | fan motor 1:actual speed
| C14 | Heating mode/defrosting period | 45Min | 1~90 | TEMP2 | 1014 | U15 | fan motor 2:actual speed
| C15 | Heating mode/ defrosting max. duration | 8Min | 1~20 | TEMP2 | 1015 | U16 | Driver PCB temperature
| C16 | Slide defrosting starting low pressure/high point | 5bar | 1~20 | TEMP4 | 1016 | U17 | Driver PCB state
| C17 | Slide defrosting starting low pressure/low point | 2.5bar | 1~20 | TEMP4 | 1017 | protection/error | error code
| C18 | Slide defrosting starting ambient temperature/high point | 2℃ | -10~10 | TEMP3 | 1018 | Standby | None
| C19 | Slide defrosting starting ambient Temperature/low point | -15℃ | -30~10 | TEMP3 | 1019 | Normal start-up | None
| C20 | Enable slide defrosting (0 No 1 Yes) | 1 | 0~1 | TEMP2 | 1020 | Inlet sensor failure | P01
| C21 | Enable auxiliary electric heater when defrosting (0 No 1 Yes) | 0 | 0~1 | TEMP2 | 1021 | Outlet sensor failure | P02
| C22 | Defrosting frequency | 70 | 0-90 | TEMP2 | 1022 | Ambient sensor failure | P04
| C23 | PFC function (0 No 1 Yes) | 1 | 0~1 | TEMP2 | 1023 | Suction sensor failure | P07
| C24 | Reserved | reserved | 0~1 | TEMP2 | 1024 | Exhaust sensor failure | P08
| C25 | Max. manual room number | 0 | 0~30 | TEMP2 | 1025 | Suction pressure sensor failure | PP1
| E01 | Electronic expansion valve 1 adjustment (0 Manual 1 Auto) | 1 | 0~1 | TEMP2 | 1026 | Exhaust pressure sensor failure | PP2
| E02 | Electronic expansion valve 1/ target overheat temperature (heating mode) | 5℃ | -10~10 | TEMP3 | 1027 | High pressure protection | E01
| E03 | Target overheat compensation value 1 | 1℃ | -10~10 | TEMP3 | 1028 | Low pressure protection | E02
| E04 | Target overheat compensation value 2 | 0.5℃ | -10~10 | TEMP3 | 1029 | Water flow switch protection | E03
| E05 | Electronic expansion valve 1/ initial steps (heating mode) | 350 | 0~480 | TEMP4 | 1030 | anti-freezing protection: Winter level 1 | E19
| E06 | Initial step compensation 1 | 0 | 0~200 | TEMP4 | 1031 | anti-freezing protection: Winter level 2 | E29
| E07 | Initial step compensation 2 | 0 | 0~200 | TEMP4 | 1032 | Anti-freezing protection | E07
| E08 | Initial step compensation 3 | 0 | 0~200 | TEMP4 | 1033 | Exhaust over-temperature protection | P81
| E09 | Electronic expansion valve min. steps | 100 | 0~200 | TEMP4 | 1034 | Low ambient temperature protection | E44
| E10 | Electronic expansion valve defrosting steps | 480 | 0~480 | TEMP4 | 1035 | AC input under-voltage protection | E21
| E11 | Electronic expansion valve 1/ target overheat (Cooling Mode) | 6℃ | -10~10 | TEMP3 | 1036 | AC input over-current protection (shutdown) | E22
| E12 | Target overheat compensation 1 | 0.5℃ | -10~10 | TEMP3 | 1037 | AC input over-current protection (alarm) | E23 (Not displayed)
| E13 | Target overheat compensation 2 | 1℃ | -10~10 | TEMP3 | 1038 | DC bus over-voltage protection | E24
| E14 | Electronic expansion valve 1 initial steps (Cooling Mode) | 350 | 0~480 | TEMP4 | 1039 | DC bus under-voltage protection | E25
| E15 | Initial step compensation 1 | 0 | 0~200 | TEMP4 | 1040 | IPM over-current protection | E27
| E16 | Initial step compensation 2 | 0 | 0~200 | TEMP4 | 1041 | IPM module overheating protection | E28
| E17 | Initial step compensation 3 | 0 | 0~200 | TEMP4 | 1042 | Radiator temperature sensor failure | E29
| E18 | Start time of exhaust auxiliary control | 6 | 0~100 | TEMP2 | 1043 | Power component overheating protection (shutdown) | E30
| E19 | Start time of suction overheat control | 4 | 0~100 | TEMP2 | 1044 | Power component overheating protection (alarm) | E31 (Not displayed)
| E20 | Electronic expansion valve control/ value P | 5 | 0~100 | TEMP2 | 1045 | IPM current sampling | E32
| E21 | Electronic expansion valve control/ value I | 3 | 0~100 | TEMP2 | 1046 | Compressor over-current protection (shutdown) | E33
| E22 | Electronic expansion valve control/ value D | 0 | 0~100 | TEMP2 | 1047 | Compressor over-current protection (alarm) | E34 (Not displayed)
| E23 | Water pump manual starting | 0 | 0~1 | TEMP2 | 1048 | Input voltage phase loss | E35
| E24 | Manual compressor frequency | 0 | 0~90 | TEMP2 | 1049 | Compressor start-up failure | E36
| E25 | Manual initial steps | 0 | 0~550 | TEMP2 | 1050 | Communication failure between DSP and communication board | E37
| F01 | Power-off memory (0 No 1 Yes) | 1 | 0~1 | TEMP3 | 1051 | Communication failure between DSP and PFC | E38
| F02 | Quantity of system | 0 | 0~1 | TEMP3 | 1052 | Input voltage sampling | E39
| F03 | Electric heater (0 No 1 Yes) | 0 | 0~1 | TEMP3 | 1053 | EEPROM failure | E40
| F04 | Pump working mode (0 - ordinary/1 - special / 2 - intermittent) | 0 | 0~2 | TEMP3 | 1054 | Compressor weak magnetic protection | E41
| F05 | Water pump running interval | 30 | 0~30 | TEMP3 | 1055 | Communication failure between drive board and main board | EE8
| F06 | Water pump running duration | 3 | 0~3 | TEMP3 | 1056 | Communication failure between main board and wire controller | E08
| F07 | Max fan speed (heating mode) | 1000N | 0-2000 | TEMP2 | 1057
| F08 | Min fan speed (heating mode) | 300N | 0-2000 | TEMP2 | 1058
| F09 | Max fan speed pressure (heating mode) | 5.0bar | 0-20 | TEMP2 | 1059
| F10 | Min. fan speed pressure (heating mode) | 15.0bar | 0-20 | TEMP2 | 1060
| F11 | Max. fan speed (cooling mode) | 1000N | 0-2000 | TEMP2 | 1061
| F12 | Min. fan speed (cooling mode) | 300N | 0-2000 | TEMP2 | 1062
| F13 | Max. fan speed pressure (cooling mode) | 10bar | 0-50 | TEMP2 | 1063
| F14 | Min. fan speed pressure (cooling mode) | 30bar | 0-50 | TEMP2 | 1064
| F15 | Quantity of fan | 2 | 0~2 | TEMP2 | 1065
| F16 | Manual fan speed | 0 | 0~2000 | TEMP2 | 1066
| F17 | Reserved | reserved | 0~1 | TEMP2 | 1067
| F18 | Reserved | reserved | 0~1 | TEMP2 | 1068
| F19 | Reserved | reserved | 0~1 | TEMP2 | 1069
| F20 | Compressor model selection | 0 | 0~50 | TEMP2 | 1070
| P01 | Inlet set temperature (cooling mode) | 12℃ | P07~P08 | TEMP3 | 1071
| P02 | Inlet set temperature (heating mode) | 40℃ | P09~P10 | TEMP3 | 1072
| P03 | Return difference (Constant temperature OFF/cooling mode) | 2℃ | 0.5~10 | TEMP3 | 1073
| P04 | Temperature difference (Constant temperature ON/cooling mode) | 2℃ | 0~10 | TEMP3 | 1074
| P05 | Return difference (Constant temperature OFF/heating mode) | 2℃ | 0.5~10 | TEMP3 | 1075
| P06 | Temperature difference (Constant temperature ON/heating mode) | 2℃ | 0~10 | TEMP3 | 1076
| P07 | Min. set temperature (cooling mode) | 12℃ | 8~20 | TEMP3 | 1077
| P08 | Max. set temperature(cooling mode) | 20℃ | 20~30 | TEMP3 | 1078
| P09 | Min. set temperature(heating mode) | 30℃ | 20~30 | TEMP3 | 1079
| P10 | Max. set temperature(heating mode) | 50℃ | 30~60 | TEMP3 | 1080
| P11 | Temperature difference (electric heater ON) | 5℃ | 0.5~10 | TEMP3 | 1081
| P12 | Ambient temperature (electric heater ON) | 5℃ | -10~30 | TEMP3 | 1082
| P13 | Time delay (electric heater ON) | 30 | 0~60 | TEMP2 | 1083
| P14 | Ambient temperature without time delay (electric heater ON) | 2℃ | -30~20 | TEMP3 | 1084
| P15 | Ambient temperature compensation (0 No 1 Yes) | 0 | 0~1 | TEMP2 | 1085
| P16 | Max. offset of temperature compensation | 5℃ | 0~10 | TEMP3 | 1086
| P17 | Coefficient of temperature compensation | 10 | 1~40 | TEMP4 | 1087
| P18 | Ambient temperature of starting compensation (cooling mode) | 35℃ | 10~50 | TEMP3 | 1088
| P19 | Ambient temperature of starting compensation (heating mode) | 8℃ | -30~30 | TEMP3 | 1089
| P20 | Control on main unit by the temperature of room thermostat | 1 | 0~1 | TEMP2 | 1090
| P21 | Room thermostat temperature decreased (cooling mode) | 12℃ | 0~20 | TEMP3 | 1091
| P22 | Room thermostat temperature increased (heating mode) | 20℃ | 0~30 | TEMP3 | 1092
| P23 | Control on main unit by the mode of room thermostat | 0 | 0~1 | TEMP2 | 1093

## state list
1.Transmission Format
Baud Rate |  |  | 4800bps
Start bit |  |  | 1
Byte width |  |  | 8
Parity |  |  | N
Stop bits |  |  | 1
Slave address |  |  | 97
2.Packet Format
Address | Function |  |  | Data | CRC checksum
8bits | 8bits 03:Function of reading multi registers 16:Function of presenting multi registers |  |  | N*8bits | 16bits
3.Data types
Data Types | Description
TEMP2 | unsigned byte; length: 8 bits; unit: 1; when displaying 1, the data transmitted 1.
TEMP3 | unsigned byte; accuracy: 0.5℃; formula: T*2 + 60; temperature range: -30~97℃(when displaying 25℃, according to the above formula, the data transitted by protocol is110)
TEMP4 | unsigned byte; accuracy: 0.1bar; formula: T*10; range: 0~50bar (when displaying 25bar, according to the above formula, the data transitted by protocol is 250)
TEMP5 | unsigned byte; accuracy: 1℃; formula: T + 30; temperature range: -30~224℃
4.Mailing address
Type | modbus address list
TEMP status | Name | type | modbus
U01 | water inlet | TEMP3 | 8307
U02 | water outlet | TEMP3 | 8308
U03 | suction | TEMP3 | 8309
U04 | exhaust | TEMP5 | 8310
U05 | ambient | TEMP3 | 8311
U06 | coil | TEMP3 | 8322
U07 | low pressure | TEMP4 | 8312
U08 | high pressure | TEMP4 | 8313
U09 | electronic expansion valve | TEMP2 | 8319
U10 | actual frequency | TEMP2 | 8320
U11 | set frequency | TEMP2 | 8321
U12 | suction overheat | TEMP3 | 8323
U13 | exhaust overheat | TEMP4 | 8324
U14 | fan motor 1:actual speed | TEMP2 | 8325
U15 | fan motor 2:actual speed | TEMP2 | 8326
ON/OFF |  | 0-OFF 1-ON | 9001
mode |  | 0-COOLING 1-HEATING | 9002
target temperature setting |  | TEMP3 | 9003
Error Code | Error Name
P01 | Inlet temperature sensing failure | bit 0 | 8901
P02 | Outlet temperature sensing failure | bit 1
P04 | Ambient temperature sensing failure | bit 6
P07 | suction temperature sensing failure | bit 2
P08 | exhaust temperature sensing failure | bit 3
PP1 | exhaust pressure sensing failure | bit 5
PP2 | suction pressure sensing failure | bit 4
E01 | high pressure protection | bit 7
E02 | low pressure protection | bit 8
E03 | water flow switch protection | bit 9
E19 | anti-freezing protection:winter Level 1 | bit 12
E29 | anti-freezing protection:winter Level 2 | bit 13
E07 | anti-freezing protection | bit 11
P81 | Exhaust over-temperature protection | bit 10
E44 | Low ambient temperature protection | bit 14